# PANASONIC 5HP – NON-INVERTER vs INVERTER

### FINAL COMPARISON FOR COMMITTEE CONSIDERATION

Dear Church Committee Members,

Following our previous discussion, I have further compared the Panasonic 5HP Non-Inverter and Panasonic 5HP Inverter options based on the actual usage of our First Floor Hall, cooling performance, purchase cost, electricity consumption, maintenance, PCB replacement cost, noise level and long-term practicality.

## 1. DIRECT COMPARISON

🔴 Red mark = advantage of that particular option

| Item | Panasonic 5HP Non-Inverter | Panasonic 5HP Inverter |
| --- | --- | --- |
| Quotation | 🔴 RM6,300 | RM7,600 |
| Price Difference | 🔴 Save RM1,300 | +RM1,300 |
| Cooling Capacity | 🔴 48,500 BTU/h | 47,800 BTU/h |
| Air Volume | 1,285 CFM | 1,285 CFM |
| Rated Power Input | 🔴 4.14 kW | 4.63 kW |
| Inverter Power Range | — | 🔴 0.63–5.10 kW |
| Indoor Noise | 47 / 41 dB(A) | 47 / 41 dB(A) |
| Outdoor Noise | 58 dB(A) | 58 dB(A) |
| Chemical Service | 🔴 RM500 | RM550 |
| Indoor PCB | 🔴 RM680 | RM980 |
| Outdoor PCB | 🔴 RM680 | RM1,730 (2 pcs) |
| Potential PCB Replacement Cost | 🔴 RM1,360 | RM2,710 |
| System Complexity | 🔴 Simpler | More electronic components |
| Temperature Control | Good | 🔴 More stable |
| Partial-Load Efficiency | Lower | 🔴 Higher |
| Compressor Operation | Fixed speed | 🔴 Variable speed |

## 2. ACTUAL USAGE OF THE FIRST FLOOR HALL

The normal air-conditioner usage is approximately:

### Saturday

2:00pm – 5:00pm → 3 hours
7:00pm – 10:30pm → 3.5 hours

### Sunday

8:30am – 11:30am → 3 hours

### Total: approximately 9.5 hours per week

Based on the estimated operating cost of approximately RM2/hour:

- 3-hour session → approximately RM6

- 3.5-hour session → approximately RM7

- 9.5 hours/week → approximately RM19

- Approximately RM82/month

- Approximately RM988/year

These are estimated figures only. Actual electricity consumption will depend on cooling load, operating conditions and the actual electricity tariff.

Because our actual usage is only approximately 9.5 hours per week, the electricity-saving advantage of the Inverter may take a longer period to recover the additional RM1,300 purchase cost.

# 3. COOLING CAPACITY & AIRFLOW

### Panasonic 5HP Non-Inverter

🔴 48,500 BTU/h
1,285 CFM

### Panasonic 5HP Inverter

47,800 BTU/h
1,285 CFM

The two models have almost the same cooling capacity and exactly the same quoted airflow of 1,285 CFM.

Therefore, the Inverter's additional RM1,300 is not mainly paying for higher cooling capacity.

The main advantage of the Inverter is its ability to vary compressor speed according to the cooling demand.

# 4. ENERGY EFFICIENCY

### Non-Inverter

The compressor operates at a fixed speed and controls temperature mainly through compressor ON/OFF cycling.

🔴 Advantage: simpler operation and lower initial cost

However:

- Lower efficiency during partial-load operation

- More ON/OFF compressor cycling

- Less precise temperature control

### Inverter

The compressor can vary its speed according to the cooling demand.

🔴 Advantages:

- Better partial-load efficiency

- More stable temperature

- Can reduce compressor speed after the hall reaches the desired temperature

- Better adjustment to changing cooling demand

However, the Inverter has a higher initial purchase cost of RM1,300.

# 5. NOISE LEVEL

Because this is a worship hall, noise level is also an important consideration.

According to the Panasonic specifications:

### Non-Inverter

Indoor: 47 / 41 dB(A)
Outdoor: 58 dB(A)

### Inverter

Indoor: 47 / 41 dB(A)
Outdoor: 58 dB(A)

Therefore:

There is no significant noise-level difference between the two models based on the quoted specifications.

# 6. MAINTENANCE & PCB COST

This is an important consideration for long-term maintenance.

### Panasonic 5HP Non-Inverter

Indoor PCB: RM680
Outdoor PCB: RM680

### Potential total PCB replacement:

🔴 RM1,360

### Panasonic 5HP Inverter

Indoor PCB: RM980
Outdoor PCB: RM1,730 (2 pcs)

### Potential total PCB replacement:

RM2,710

### Difference:

RM2,710 − RM1,360 = RM1,350

Therefore, the potential PCB replacement cost is approximately RM1,350 higher for the Inverter.

This does not mean that the PCB will definitely fail. It is only a consideration of the potential future repair cost.

Considering our previous experience with PCB problems, this is an important factor when looking at long-term maintenance.

# 7. CHEMICAL SERVICE COST

Contractor's quoted chemical service cost:

### 5HP Non-Inverter

🔴 RM500

### 5HP Inverter

RM550

Difference:

RM50 per service

Therefore, the maintenance chemical-service difference is relatively small.

# 8. EXISTING COPPER PIPE & ELECTRICAL WIRING

The contractor has confirmed that the existing copper piping and electrical wiring can be reused for the new 5HP unit.

Therefore:

🔴 No additional copper-pipe replacement cost

🔴 No additional wiring cost

🔴 No additional RM2,590 piping cost

This will also help reduce installation time and allow the contractor to proceed faster.

# 9. FUTURE SPARE PARTS / CASSETTE-TYPE NON-INVERTER

According to the information provided by the contractor, the government restriction expected next year applies to wall-mounted non-inverter air-conditioners, while cassette-type non-inverter units are not affected in the same way.

Therefore, according to the contractor, cassette-type non-inverter air-conditioners should continue to have spare-parts and service support.

This is an important point to consider because our proposed unit is a cassette-type 5HP Non-Inverter.

# 10. MAIN ADVANTAGES OF EACH OPTION

## 🔴 PANASONIC 5HP NON-INVERTER – RM6,300

🔴 Lower purchase price – save RM1,300

🔴 Higher cooling capacity – 48,500 BTU/h

🔴 Same airflow – 1,285 CFM

🔴 Lower potential PCB replacement cost – RM1,360

🔴 Lower chemical service cost – RM500

🔴 Simpler system

🔴 Potentially easier and less costly future troubleshooting

🔴 Suitable for our relatively limited usage of approximately 9.5 hours/week

🔴 Same quoted noise level as Inverter

🔴 Existing copper pipe and wiring can be reused

Main disadvantage:

❌ Lower energy efficiency compared with Inverter
❌ Less precise temperature control
❌ Fixed-speed compressor

## 🔴 PANASONIC 5HP INVERTER – RM7,600

🔴 Variable-speed compressor

🔴 Better temperature stability

🔴 Better partial-load energy efficiency

🔴 Can adjust cooling according to actual cooling demand

🔴 Same 1,285 CFM airflow

🔴 Same quoted noise level as Non-Inverter

Main disadvantages:

❌ RM1,300 higher purchase price

❌ Higher potential PCB replacement cost

❌ Indoor PCB: RM980

❌ Outdoor PCB: RM1,730 for 2 pcs

❌ Potential total PCB replacement: RM2,710

❌ More electronic components and greater system complexity

❌ Our actual usage is only approximately 9.5 hours/week

# 11. MY PERSONAL RECOMMENDATION

After comparing the two options based on:

- Purchase cost

- Cooling capacity

- Airflow

- Actual usage hours

- Estimated electricity cost

- Noise level

- Chemical service cost

- PCB replacement cost

- System complexity

- Future maintenance

- Existing piping and wiring

### My suggestion this time is:

# 🔴 PANASONIC 5HP NON-INVERTER

### 🔴 RM6,300

My recommendation is not simply because it is cheaper.

I feel the 5HP Non-Inverter gives our church a practical balance between cooling performance, reliability, maintenance and cost.

It provides:

48,500 BTU/h + 1,285 CFM

while the Inverter provides:

47,800 BTU/h + 1,285 CFM

Our hall is also only normally using the air-conditioner for approximately 9.5 hours per week.

Therefore, I feel that the additional RM1,300 for the Inverter may take a relatively long time to recover through electricity savings.

At the same time, the Non-Inverter has:

- Lower purchase cost

- Lower chemical service cost

- Lower potential PCB replacement cost

- Simpler system

- Slightly higher cooling capacity

- Same airflow

- Same quoted noise level

The Panasonic 5HP Inverter at RM7,600 remains a good option if the Committee considers energy efficiency and temperature stability to be the higher priority.

However, based on the overall balance, my personal recommendation is the Panasonic 5HP Non-Inverter at RM6,300.

# 12. FINAL DECISION

I would like to hear everyone's opinions before we make the final decision.

Once the Committee agrees on the selected model, we should:

- Confirm the model immediately

- Place the order immediately

- Confirm stock availability

- Arrange installation urgently

- Reuse the existing copper piping and electrical wiring

- Push the contractor to complete the installation before this Sunday

The objective is to select the most suitable and practical solution for our First Floor Hall, while ensuring that our Sunday School and worshippers can have a comfortable worship environment.

Thank you everyone for your consideration and valuable input. 🙏